|  | KJF204 |
| --- | --- |
| W-PAK S Series Filter has wide range of efficiencies and rigid compact designs make this an excellent product for upgrading current system and for new installation. The filters are used in a wide variety of applications. They are ideally suited for Hospital, Automotive painting System pr in any critical application while high efficiency is essential, and fiber shedding can not be tolerated. The medial is extremely durable and non-shedding. | Testing Method 測試方法 Dot Spot Efficiency (in NBS Testing Method) 比色法 Arrestance (in AFI Testing Method) 比重法 MERV 90~95% > 99% 14 80~85% > 98% 13 60~65% > 97% 11 45~50% > 96% 9 By ASHRAE Standard 52.1-1992 (Equal to EN 779) 依ASHRAE 52.1-1992標準 (德國EN 779) By ASHRAE 52.2-1999 Standard 依ASHRAE 52.2-1999標準 ASHRAE Grade S Series W-PAK Extended Surface Air Filter- Synthetic Fiber 中性能W-PAK型空氣過濾網 - 合成纖維 Features: W-PAK S Series filter contains moisture-resistant pleat stabilizers on both sides of the media pack. This ensures that the tapered pleat configuration will not be deformed throughout the service life of the filter. The design of the pleat stabilizer offers maximum media filtration area and dust holding capacity, furthermore extending filter life span. Efficiency: Per ASHRAE 52.1-1992 standard (equal to EN779), the filters have an average atmospheric dust spot efficiency range 45-50%, 60-65%, 80-85% and 90-95% (in NBS Test Method); per ASHRAE 52.2, the efficiency is MERV9, MERV11, MERV12 & MERV14. |

KJF204

Media: W-PAK S-Series filters are manufactured of Multiple Layers Synthetic Microfiber formed into a pleated configuration. The Synthetic Microfiber builds up in non-woven layers to strengthen Multi-layers and eliminate fiber shedding. It contains non-glass fiber (to be thought a healthy hazard). W-PAK S-Series filters are not affected by extreme moisture and humidity conditions, unlike wet glass fibers that will be lost up to 20% efficiency. The media is color coded by efficiency. Media Color Average Efficiency (NBS) Average Arrestance (AFI) Tan 45~50% 90% Orange 60~65% 97% Pink 80~85% 98% Yellow 90~95% 99% Backings: Class 1 – Woven Glass Scrim Class 2 – Non-Woven Polyester or Nylon Media Support Grid: A corrosion-resistant metal support grid is bonded to the media to strengthen pleat construction and stability. Frame: The enclosing frame is a galvanized steel construction. Diagonal supports on both upstream and downstream sides enhance the construction of the filter. This construction provides W-PAK filter with exceptional strength and durability for a longer life span. It is available in header or non-header type. 特色：中性能W-PAK濾網於濾材兩面有防潮之固定隔板，濾材褶狀結構不變形，此設計使濾網具有大的過濾面積與集塵能力，延長濾網壽命。 效率：依ASHRAE 52.1-1992標準法測試，濾網具比色法效率45-50%、60-65%、80-85%、90-95%可供選擇。 濾材：由多層合成纖維所製成之褶形結構，多層合成纖維被覆布強化過濾層及避免纖維的脫落。非玻璃纖維材(被認為有害健康)。不受高濕度影響，不像玻璃纖維潮濕時，會喪失其效率高達20%。濾材以抗腐蝕金屬被覆於後，強化褶形結構與韌性。 外框：框材可選用紙框、鍍鋅鐵框、鋁框或不銹鋼框。鍍鋅鐵製外框結構，於上風與下風處對角支撐設計，增加W-PAK過濾網之強度及耐久性。

KJF204

Performance Data – ASHRAE Grade S Series Extended Surface Air Filter（Synthetic Fiber） 中效率濾網性能 - W-PAK型空氣濾網（合成纖維） Efficiency Nominal Size Actual Size Rated Capacity Pressure Drop 效率 通稱尺寸 實際尺寸 額定風量 壓力損失 ％ (W*H*D) (W*H*D) CMH Pa Dot Spot Efficiency (in NBS) 比色法 Arrestance (in AFI) 比重法 （inch） （mm） Initial Resistance 初壓損 Final Resistance 末壓損 90~95 ＞ 99 12*24*4 289*595*95 850 134 250 24*24*4 595*595*95 1700 12*24*6 289*595*150 1020 169 324 24*24*6 595*595*150 2040 12*24*12 289*595*292 1700 129 24*24*12 595*595*292 3400

KJF204

80~85 ＞ 98 12*24*4 289*595*95 850 90 250 24*24*4 595*595*95 1700 12*24*6 289*595*150 1020 116 324 24*24*6 595*595*150 2040 12*24*12 289*595*292 1700 88 24*24*12 595*595*292 3400 60~65 ＞ 97 12*24*4 289*595*95 850 46 250 24*24*4 595*595*95 1700 12*24*6 289*595*150 1020 90 324 24*24*6 595*595*150 2040 12*24*12 289*595*292 1700 67 24*24*12 595*595*292 3400 45~50 ＞ 96 12*24*4 289*595*95 850 42 250 24*24*4 595*595*95 1700 12*24*6 289*595*150 1020 70 324 24*24*6 595*595*150 2040 12*24*12 289*595*292 1700 44 24*24*12 595*595*292 3400 1. Recommended Final Resistance on all S Series Filters is 1.5” w.g. 2. Special Sizes are available upon request. ※特殊規格可生產製造。

KJF204

Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction 總成 Media 濾材 Synthetic Fiber 合成纖維 Frame Material 外框材質 Card Board 紙框 Metal Frame 金屬框 Frame Type 外框型式 Box Type 箱型 Single Header 單法蘭 Support Grid 支撐網 Anticorrosion Metal Support Grid w/Radial Wedge Pleats 抗蝕性的金屬支撐網，採楔行結構 Service Conditions 使用條件 The maximum continuous use temperature 連續使用最高溫度 ℃ 60 Instant Highest Humidity 使用瞬間最高濕度 % RH 98（No condensation state） 98（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net